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Nominal Data 



Project1
Unit
Rating
Nominal Voltage :
[VAC]
220
Voltage Range :
[VAC]
200~277
Frequency :
[Hz]
50/60
Speed :
[rpm]
1080±10%
Current :
[A]
0.72±16%
Power input :
[W]
100±16%
Air flow (Max) :
[m3/h]
4223±10%

[CFM]
2484±10%
Static pressure ( Max) :
[Pa]
80±10%
Noise level (LpA ):
dB(A)
66±6
Max.ambient Temp :
℃
60
Min.ambient Temp :
℃
-20
Insulation Class :

Class F
Protection Type :

IP54
Work system :
  
S1



















	

Technical Features 
Production Reference standard
GB12350《Safety requirements of small power motors》
JB/T10562 《 Technical specification for general purposes axial fans》
EN60335-1《Household and similar electrical appliances-safety》
ISO5801-1997《Industrial fans-performance testing using standardized airways》
GB/T2888《Methods of Noise Measurement for Fans Blowers Compressors and Roots Blowers》
Certification
CE
Environmental protection
RoHS、Reach





Technical Features 



Service environment
Operating temperature：-20~60℃；Operating humidity：30 ~ 95 % RH
Storing temperature：-25 ~ 60℃；Storing humidity：30 ~95 % RH
Applicable altitude range：＜1000m  
Life Expectance
40,000Hours(L10)，At 40℃ room, humidity 15%~65%RH.
Balancing
According to JB/T 9101-1999 requirements G6.3
Vibration of the fan
Test method accord with JB/T 8689
Installation method
Horizontal or vertical installation
Material
PA6 +30%GF ( Impeller )  
Bearing
Maintenance-free deep groove ball bearings
Weight
APPROX / (Kg)  
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Speed Control
Control input 0~10VDC/PWM
VSP Control
Control signal VSP voltage range1.5±0.5VDC~9±0.5VDC
(During normal operation, when the VSP voltage is below 1.2VDC, the motor switches from operating mode to standby mode)
PWM Control 
PWM signal: frequency 1K～10KHz, amplitude 10V,duty cycle 12%～100% .
Signal Output
Tach output：1 Pulse/R；FG internal open circuit output, external pull-up resistor R, pull-up voltage V+
Auxiliary power output
Output 10VDC，Max Current 10mA
Protection 
Current limiting protection 、Over-temperature protection、Over-current protection
Locked-rotor protection
Soft start
Delay time <30 seconds to full speed
Serial Communication
/



 Electrical Protection




 Product Drawing
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Wiring Diagram 




Label 

L
Color
Function 
Functional description
L1
Yellow/Green
PE
Ground lead

Brown
L
Live line

Blue
N
Naught line

Yellow
Speed Control
Speed regulation signal input terminal,0-10VDC voltage /PWM 

White
FG
Velocity feedback pulse output 1 Pulse/R

Red
+10VDC
Fixed voltage output 10VDC,Max 10mA

Blue
GND
Ground reference end of control signal
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Confirm by sales team when placing sample order or bulk order 

          

    







Charts :Air Flow (P-Q)





















电流≦  mA不能用于***，上电顺序要求


Confirm by sales team when placing sample order or bulk order 
Label 


Warning:

1.The fan and motor must be used within the prescribed scope of temperature and humidity otherwise it will cause an unexpected damage. 
2. Fan is not set wrong connection protection，Provide the right voltage and line sequence according to the nameplate otherwise it will damage the product. 
3. Wiring depends on the wiring diagram and please connect the earth ground if required. We don't suggest to use the extension cord .Any wrong connection may cause the damage of the fan. 
4. Be careful when moving the fan and do not take the blades as a handle because it will cause the distortion and chatter. 
5. Connect the thermostat if required otherwise it would damage the motor because of the over temperature. 
6. The length of the mounting screws shall not exceed the requirement, otherwise the fan will be damaged. 
7. Do not disassemble the fan arbitrarily. It may hurt the capacity of water tightness and dynamic balance or cause other serious problems. 
8. The over current protector is necessary in case the damage from the over current. 
9. Install the fan as required, any other installing direction would affect the service life of the product. 
10. The fan with inlet ring should be installed follow the requirements or it will affect the performance. 
11. Users should use the standard cable when install the fan otherwise it will affect the water tightness. 
12. The fan should keep away from the children especially the blade and electric parts .And the children are not allowed to operate the fan alone. 
13. Do not connect the white signal cable directly to the red signal cable or the external DC power supply. Otherwise, the fan may be damaged.T
14.Please do not perform extraction and insertion of the connector under revolution irrespective of power on and power on and power off , and the fan should not touch or move when running. 

15. Do not lift the fan wire when taking the fan, and do not impact the bearing during the handling process. 
16. The version change may not be notified, please ask our company for the latest version when necessary.

17.Please be informed that we are not responsible for any damage or accidents caused by violating above rules to install and operate the fan. 


     Rs485
Approval 
Note :Please check and mark the data when you sign the specification sheet .
Product Data Confirm :
0-10V
PWM
Speed Control System :

DATE :

CUSTOMER SIGNATURE:

CUSTOMER APPROVAL

P-Q Curve
①	
4349.1	3973.2	3534.3	2690.1	2237.55	1680	0	16.8	32.55	61.95	69.3	78.75	10V	②	
4066.65	3756.9	3244.5	2615.55	2134.65	1680	0	13.65	31.5	53.55	64.05	74.55	7V	③	
3040.8	2718.45	2340.45	1901.55	1638	0	0	9.45	19.95	29.4	32.55	80.85	5V	④	
Air Volume ( m3/h )

Static Air Pressure  (Pa)
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